## Instructions
FacilityOS — Equipment & Communication Survey
Digitalsystem Technology Inc. · 1470 Valley Vista Dr, Ste 204, Diamond Bar, CA 91765 · 888-969-8809 · support@digitalsystem.net · https://www.digitalsystem.net
Document FOS-DOC-102 · Revision 1.0 (2026-10-14)
Purpose
This workbook collects what Digitalsystem needs to connect your site to FacilityOS: contacts, the gateway's network plan, every device and how it communicates, and the points to monitor. It accompanies the Site Onboarding Readiness Checklist (FOS-DOC-101).
How to fill it in
1. Site & Contacts: site details and one row per contact.
2. Network: the gateway's hardware, IP plan, any additional gateways and the firewall rules (pre-filled; confirm or correct).
3. Equipment Inventory: one row per device. Use the dropdowns for System, Equipment type, Protocol and the Yes/No columns. If the site has several gateways, the Gateway column says which gateway (or building / area) serves the device. The grey italic rows are examples — overwrite or delete them.
4. Point List: one row per point, in the same format as the platform's point schedule. Row 1 must stay exactly as it is; row 2 (starting with #) is help text and is ignored on upload. To upload: save this sheet as "CSV UTF-8" and upload it in FacilityOS under Engineering → Point schedule. The platform checks every line before anything changes.
5. Send the workbook to your Digitalsystem project manager or support@digitalsystem.net. Never put passwords, communities, keys or certificates in this workbook (the platform refuses them in the point schedule) — just mark "Credentials needed". Device credentials are entered directly in FacilityOS by the engineer, per device, and delivered encrypted to the gateway that serves the device.
Protocols FacilityOS connects to
BACnet/IP (MS/TP via a BACnet router, BACnet/SC), Modbus TCP and Modbus RTU, SNMP v3 (and v1/v2c read-only), OPC UA; read-only: MQTT, DL/T 645, IEC 60870-5-104, IEC 61850 (protection relays, recorders and PQ analysers are never operated), wired M-Bus, EtherNet/IP; KNXnet/IP (setpoints writable); ONVIF cameras for alarm snapshots. Anything else needs a protocol gateway — choose "Other (gateway needed)".
Units
FacilityOS stores values in US customary units (°F, psi, gpm, cfm, inWC, kW). Convert metric values before entering them in the Point List.

## Site & Contacts
Site
Customer
Site name
Street address
City, state, ZIP
Facility type
Time zone
Site access / badge process
Hours of operation / maintenance windows
Prepared by
Date
Contacts
Role | Name | Company | Phone | After-hours phone | E-mail | Notes
Facility manager (project owner)
Second approver (manager)
Shift lead / chief engineer
IT / network
OT / cyber-security
BMS / controls contractor
Electrical contractor
Equipment vendor
Remote hands / site access

## Network
Gateway
Gateway ID (from FacilityOS)
Host name
Make / model
Serial number
CPU architecture (x86_64 / ARM64)
Operating system
MAC address – uplink
MAC address – OT
Location / rack / U
Power circuit / UPS outlet
Platform host name (from Digitalsystem)
NTP servers
DNS servers
IP plan
Interface | VLAN | IP address / prefix | Default gateway | Static routes | Switch / port | Notes
Uplink (to platform)
OT (field devices)
Out-of-band (optional)
Additional gateways (large sites and campuses: one per building, plant area or OT segment)
Gateway ID / host name | Building / area served | Uplink IP / VLAN | OT IP / VLAN | Location / rack | Make / model | Notes
(primary gateway — above)
Every gateway needs the same outbound rules below (TCP 443 and 4222 to the platform, NTP, DNS) from its own uplink.
Firewall rules (gateway outbound only; no inbound rules)
Source | Destination | Port / protocol | Purpose | Approved by | Date | Notes
Gateway uplink | Platform host | TCP 443 | Installer and software download (HTTPS proxy allowed)
Gateway uplink | Platform host | TCP 4222 | Gateway connection, TLS; direct, no proxy
Gateway uplink | NTP servers | UDP 123 | Time synchronisation (required)
Gateway uplink | DNS servers | UDP/TCP 53 | Name resolution
Gateway OT | BACnet devices / BBMD | UDP 47808 | BACnet/IP
Gateway OT | Modbus devices / converters | TCP 502 | Modbus TCP
Gateway OT | UPS / PDU cards | UDP 161 | SNMP v3 (v1/v2c read-only)
Gateway OT | OPC UA servers | TCP 4840 | OPC UA
Gateway OT | MQTT broker | TCP 8883 | MQTT over TLS, if used (clear-text 1883 only if enabled on the gateway)
Gateway OT | IEC 104 RTU | TCP 2404 (19998 TLS) | IEC 60870-5-104, if used
Gateway OT | KNX IP interface | UDP 3671 | KNXnet/IP, if used
Gateway OT | EtherNet/IP controllers | TCP 44818 | EtherNet/IP, if used
Gateway OT | IP cameras | Camera's ONVIF port (often TCP 80 / 443) | Alarm snapshots (video linkage), if used

## Equipment Inventory
ID | System | Equipment type | Location | Gateway (building / area served) | Make | Model | Serial | Protocol | IP / MS-TP MAC | BACnet device instance / Modbus unit ID | Port | Credentials needed | Comm card needed | Converter needed | Points list available? | Owner / contractor | Notes
CH-1 | Cooling plant | Chiller | Central plant, B1 | GW-1 (central plant) | Trane | CenTraVac CVHF | (serial) | BACnet/IP | 10.20.1.11 | 1101 | UDP 47808 | No | No | No | Yes | ACME Controls (BMS) | Example. Tracer UC800 controller; confirm BACnet/IP is enabled
CHWP-1 | Cooling plant | VFD | Pump room, B1 | GW-1 (central plant) | ABB | ACH580 | (serial) | Modbus TCP | 10.20.2.21 | 1 | TCP 502 | No | Yes | No | Yes | Mechanical contractor | Example. Modbus TCP needs the drive's Ethernet adapter option; or Modbus RTU on its built-in RS-485
UPS-A | Critical power | UPS | Electrical room 1 | GW-1 (central plant) | Eaton | 9395 | (serial) | SNMP v3 | 10.20.6.81 |  | UDP 161 | Yes | Yes | No | Yes | UPS service vendor | Example. Network card with SNMPv3 read-only user (authPriv SHA/AES)
MSB-1-PM | Electrical distribution | Power meter | Main switchboard MSB-1 | GW-1 (central plant) | Schneider Electric | PowerLogic PM8000 | (serial) | Modbus TCP | 10.20.7.21 | 1 | TCP 502 | No | No | No | Yes | Electrical contractor | Example. Register map and word order from the meter manual
VAV-101 | Air side / HVAC | VAV box | Level 1, east | GW-2 (office building) | Distech Controls | ECB series | (serial) | BACnet MS/TP (via router) | net 5 / MAC 12 | 5012 | UDP 47808 | No | No | Yes | Yes | ACME Controls (BMS) | Example. Reached through BACnet router 10.20.1.5

## Point List
device_id | device_name_zh | device_name_en | device_type | area | protocol | endpoint | vendor | model | point_key | label_zh | label_en | unit | dtype | role | writable | risk | min | max | safe_value | bacnet_object | bacnet_instance | bacnet_property | modbus_table | modbus_address | modbus_type | modbus_order | modbus_bit | scale | offset | snmp_oid | opcua_node | true_values | active_values | gateway | scan | mqtt_topic | mqtt_json | mqtt_ts | sparkplug | sparkplug_metric | dlt645_di | dlt645_format | iec104_ioa | iec104_type | mbus_record | mbus_units | knx_ga | knx_dpt | knx_status_ga | enip_tag | enip_type | stale_after | iec61850_ref | iec61850_fc | dnp3_group | dnp3_index | s7_addr | s7_type | firmware | serial
# Required. Device ID: letters, digits, - _ (max 48), e.g. CH-1. Lines starting with # are ignored on upload | Chinese name (optional) | English name | Required. e.g. Chiller, Pump, CRAH (letters first, max 32) | cooling, airside, liquid, power, heating, process, refrigeration, utilities, lighting, life_safety, materials, medical, cleanroom, water, gases, exhaust | Required. Pick from the list (14 protocols) | BACnet host[:47808][/instance]; Modbus host[:502][/unit]; SNMP host[:161]; opc.tcp://host:4840; rtu:/dev/ttyUSB0?baud=9600&parity=N&stop=1&unit=3; snmp2c://host; mqtts://broker:8883; dlt645:/dev/ttyUSB1?baud=2400&parity=E&addr=…; iec104://host:2404?ca=1; mbus:/dev/ttyUSB2?baud=2400&addr=5; knx://host:3671; enip://plc?slot=0; iec61850://ied:102?rcb=PROT/LLN0.BR.brcbST01&sync=ptp. Never a password | Make | Model | Required. Point key, e.g. CHWS_T | Chinese label | English label | US units only: °F, ΔF, psi, inWC, gpm, cfm, kW, kWh, %, %RH … | Required. REAL or BOOL | run, fault, hoa, alarm, setpoint, status or empty | never / approval / operator. Only BACnet, Modbus TCP/RTU, OPC UA and KNX setpoints can be writable | 1, 2 or 3 | Minimum (required if writable) | Maximum (required if writable) | Modbus/OPC UA writable points: value when a PLC program lets go; empty = restore the earlier value | AI AO AV BI BO BV MSI MSO MSV | Object instance | Default present-value | holding / input / coil / discrete | 0-based (40001 = holding 0) | int16 uint16 int32 uint32 float32 | AB/BA (16-bit); ABCD/CDAB/BADC/DCBA (32-bit) | 0–15 for a BOOL inside a register | value = raw × scale + offset | Offset | e.g. 1.3.6.1.2.1.33.1.4.4.1.5.1 | e.g. ns=2;s=Meter.kW | BOOL: raw values meaning true, e.g. 4 | REAL hoa/run/fault/alarm: active values, e.g. 1¦2 | Gateway ID that reaches the device; empty = the site's primary gateway | control = control period (100–500 ms); monitor or empty = monitoring period (1–5 s) | MQTT: one exact topic, no + or #, e.g. site1/ahu/1/telemetry | MQTT: JSON path of the value, e.g. $.temp | MQTT: optional JSON path of the time stamp, e.g. $.ts | Sparkplug B: group/edge-node[/device], e.g. plant1/edge-node-3/cdu9 (instead of mqtt_topic) | Sparkplug B: metric name from the BIRTH, e.g. Supply/Temp | DL/T 645: data identifier, MSB first: 02010100 (2007) or B611 (1997) | DL/T 645: format from the meter manual (e.g. XXX.X) if not built in | IEC 104: information object address 1–16777215 | IEC 104: monitoring type, e.g. M_ME_NC_1, M_SP_NA_1 | M-Bus: record, e.g. energy, volume, flow_temp, energy:s1, #3 | M-Bus: us (converted, default) or native | KNX: group address, e.g. 3/1/1 | KNX: datapoint type, e.g. 9.001; writable only 9.001 / 5.001 | KNX: status group address (read-back), e.g. 3/3/1 | EtherNet/IP: Logix tag, e.g. Program:CHW.DiffPress | EtherNet/IP: data type, e.g. REAL, DINT, BOOL | MQTT / IEC 104 / KNX devices: stale after no update for this long, e.g. 300 or 5m | IEC 61850: object reference LD/LN.DO.DA, e.g. PROT/XCBR1.Pos.stVal (read-only) | IEC 61850: functional constraint ST, MX, SP, SV, CF, DC, SG, SE, SR, OR, BL or EX (never CO) | DNP3: static object group 1, 3, 10, 20, 21, 30 or 40 | DNP3: point index within the group (0–65535) | Siemens S7: STEP 7 address, e.g. DB10.DBD4, DB10.DBX0.0, MW10 | Siemens S7: data type (optional), e.g. REAL, DINT, INT | Firmware the device reports (nameplate, BACnet firmware-revision), e.g. 4.30; selects the point-map generation | Nameplate serial number (copied to the CMMS asset)
CH-1 | 冷水机组 1 | Chiller 1 | Chiller | cooling | BACnet/IP | 10.20.1.11:47808/1101 | Trane | CVHF 800 | CHWS_T | 冷冻水供水温度 | Chilled water supply temp | °F | REAL |  | never | 1 | 38 | 60 |  | AI | 4
CHWP-1 | 冷冻水泵 1 | CHW pump 1 | Pump | cooling | Modbus TCP | 10.20.2.21:502/1 | ABB | ACH580 | SPD_SP | 转速设定值 | Speed setpoint | % | REAL | setpoint | approval | 2 | 30 | 100 | 60 |  |  |  | holding | 2 | int16 | AB |  | 0.1
UPS-A | UPS A | UPS A | UPS | power | SNMP v3 | 10.20.6.81:161 | Eaton | 9395 | LOAD | 输出负载率 | Output load | % | REAL |  | never | 1 | 0 | 100 | [11 empty] | 1.3.6.1.2.1.33.1.4.4.1.5.1
EF-2 | 排风机 2 | Exhaust fan 2 | Fan | exhaust | Modbus RTU | rtu:/dev/ttyUSB0?baud=9600&parity=N&stop=1&unit=3 | Danfoss | FC 102 | SPD_SP | 转速设定值 | Speed setpoint | % | REAL | setpoint | approval | 2 | 20 | 100 | 50 |  |  |  | holding | 2 | int16 | AB |  | 0.1 | [5 empty] | SITE-GW2 | control
IAQ-3 | 空气质量传感器 3 | Air quality sensor 3 | Sensor | airside | MQTT | mqtts://10.20.8.5:8883 |  |  | CO2 | 二氧化碳 | CO2 | ppm | REAL |  | never | 1 | 0 | 5000 | [17 empty] | site1/iaq/3/telemetry | $.co2 | $.ts | [13 empty] | 5m
MTR-7 | 配电电表 7 | Panel meter 7 | Meter | power | DL/T 645 | dlt645:/dev/ttyUSB1?baud=2400&parity=E&addr=000012345678 | Chint | DTSU666 | KWH | 正向有功电能 | Forward active energy | kWh | REAL |  | never | 1 | [24 empty] | 00010000
RM-101 | 会议室 101 | Meeting room 101 | Room | airside | KNX | knx://10.20.11.4:3671 | MDT | SCN-IP100 | TEMP_SP | 室温设定 | Room setpoint | °F | REAL | setpoint | operator | 1 | 64 | 78 | [28 empty] | 3/2/1 | 9.001 | 3/3/1

## Lists (hidden)
ListProtocol | ListSystem | ListType | ListYesNo | PtProtocol | PtArea | PtType | PtUnit | PtDtype | PtRole | PtWritable | PtRisk | PtBacObj | PtMbTable | PtMbType | PtMbOrder | PtScan | PtMbUnits | PtIec104 | PtKnxDpt | PtEnip
BACnet/IP | Cooling plant | Chiller | Yes | BACnet/IP | cooling | Chiller | °F | REAL | run | never | 1 | AI | holding | int16 | AB | control | us | M_SP_NA_1 | 1.001 | BOOL
BACnet MS/TP (via router) | Air side / HVAC | Cooling tower | No | Modbus TCP | airside | CoolingTower | ΔF | BOOL | fault | approval | 2 | AO | input | uint16 | BA | monitor | native | M_DP_NA_1 | 1.002 | SINT
BACnet/SC | White space cooling | AHU | Unknown | SNMP v3 | liquid | AHU | % |  | hoa | operator | 3 | AV | coil | int32 | ABCD |  |  | M_ME_NA_1 | 1.009 | INT
Modbus TCP | Liquid cooling | RTU |  | OPC UA | power | RTU | %RH |  | alarm |  |  | BI | discrete | uint32 | CDAB |  |  | M_ME_NB_1 | 1.011 | DINT
Modbus RTU (RS-485) | Heating | VAV box |  | Modbus RTU | heating | VAV | psi |  | setpoint |  |  | BO |  | float32 | BADC |  |  | M_ME_NC_1 | 5.001 | LINT
SNMP v3 | Electrical distribution | FCU |  | SNMP v2c | process | FCU | inWC |  | status |  |  | BV |  |  | DCBA |  |  | M_ME_ND_1 | 5.003 | USINT
SNMP v1/v2c | Critical power | CRAH |  | SNMP v1 | refrigeration | CRAH | gpm |  |  |  |  | MSI | [5 empty] | M_IT_NA_1 | 5.010 | UINT
OPC UA | Process utilities | CRAC |  | MQTT | utilities | CRAC | cfm |  |  |  |  | MSO | [5 empty] | M_SP_TB_1 | 7.001 | UDINT
MQTT | Refrigeration | In-row cooler |  | DL/T 645 | lighting | CDU | fpm |  |  |  |  | MSV | [5 empty] | M_DP_TB_1 | 8.001 | ULINT
DL/T 645 | Lighting | CDU |  | IEC 104 | life_safety | Boiler | kW | [10 empty] | M_ME_TD_1 | 9.001 | REAL
IEC 60870-5-104 | Life safety (monitor only) | Boiler |  | M-Bus | materials | Pump | kWh | [10 empty] | M_ME_TE_1 | 9.004 | LREAL
IEC 61850 | Medical | Pump |  | KNX | medical | VFD | MW | [10 empty] | M_ME_TF_1 | 9.006 | BYTE
M-Bus (wired) | Environment / leak | VFD |  | EtherNet/IP | cleanroom | HeatExchanger | MWh | [10 empty] | M_IT_TB_1 | 9.007 | WORD
KNXnet/IP | Energy / renewables | Heat exchanger |  | IEC 61850 | water | UPS | kVA | [11 empty] | 9.008 | DWORD
EtherNet/IP | Cleanroom / dry room | UPS |  | DNP3 | gases | BatteryMonitor | kvar | [11 empty] | 12.001 | LWORD
ONVIF (camera) | Water / UPW / wastewater | Battery monitor |  | S7 | exhaust | Generator | W | [11 empty] | 13.001
Dry contact / I/O | Gases / CDA / vacuum | Generator |  |  |  | ATS | V | [11 empty] | 13.010
Other (gateway needed) | Exhaust / abatement | ATS |  |  |  | STS | A | [11 empty] | 14.019
Unknown | Security / cameras | STS |  |  |  | Switchgear | Hz | [11 empty] | 14.056
| Other | Switchgear / breaker |  |  |  | Meter | PF | [11 empty] | 14.068
|  | Power meter |  |  |  | PDU | min
|  | Protection relay |  |  |  | RPP | s
|  | Disturbance recorder |  |  |  | RefrigerationRack | h
|  | Power quality analyzer |  |  |  | ColdRoom | rpm
|  | PDU / rPDU |  |  |  | Compressor | ft
|  | RPP / busway |  |  |  | Dryer | in
|  | Refrigeration rack |  |  |  | PLC | gal
|  | Cold room / freezer |  |  |  | Elevator | lb
|  | Air compressor |  |  |  | FireAlarm | BTU/h
|  | Dryer |  |  |  | Lighting | MBH
|  | PLC |  |  |  | LeakDetection | tons
|  | BMS controller |  |  |  | MedGas | ppm
|  | BACnet router |  |  |  | RoomMonitor | °
|  | Protocol converter |  |  |  | Sensor | ppb
|  | Elevator / escalator |  |  |  | PVInverter | µS/cm
|  | Fire alarm panel |  |  |  | BESS | MΩ·cm
|  | Lighting panel |  |  |  | Other | NTU
|  | Leak detection |  |  |  |  | pH
|  | Medical gas alarm |  |  |  |  | mg/L
|  | Room pressure monitor |  |  |  |  | Torr
|  | Temperature / humidity sensor |  |  |  |  | mTorr
|  | IAQ sensor |  |  |  |  | inHg
|  | Water / gas / BTU meter |  |  |  |  | scfm
|  | PV inverter |  |  |  |  | scfh
|  | Battery storage |  |  |  |  | ct/ft³
|  | EV charger |  |  |  |  | kV
|  | Particle counter |  |  |  |  | Ah
|  | Gas detector / GMS |  |  |  |  | mΩ
|  | Gas cabinet / VMB |  |  |  |  | lux
|  | IP camera |  |  |  |  | fc
|  | KNX room controller |  |  |  |  | gph
|  | Substation RTU (IEC 104) |  |  |  |  | lb/h
|  | MQTT broker / IoT sensor |  |  |  |  | mg/dscm
|  | Other |  |  |  |  | kscfh